Seismic Performance Evaluation of Non-Structural Elements Using Shake Table Test

Shounak Mitra1 and Kamalika Kundu2

1 Hilti India Pvt. Ltd., Gurugram 122002, Haryana, India

2 Hilti Asia Pacific Pte Ltd., Singapore 117372, Singapore

Shounak.mitra@hilti.com

Kamalika.kundu@hilti.com

Abstract. As our cities get more crowded, high-rise buildings have become a common sight. Often these buildings are covered in a labyrinth of pipes, cables and other utilities that are crucial for functioning of building services. These appendages are termed as Non-Structural Elements (NSEs) and are attached to the structural elements such as slab, beam, column, etc. During an earthquake, NSEs may sway and get damaged due to forces induced by ground motions if not secured properly. Any damage to NSEs may disrupt the building services and create blockage which may hinder evacuation. In fact, NSEs may account up to 85% of project cost depending on the type of building. A test project was carried out to evaluate performance of conventional and modular non-structural supports subject to base excitation using shake table. This paper summarizes the finding of the research program and recommends practices that may be adopted to minimize damage to NSEs during earthquake.

Keywords: Seismic, Anchors, Supports, Pipes, Cable Tray; High-rise Buildings, Shake Table Test.

# Introduction

Every building has a number of other components that are necessary for its proper operation, including its contents, its appendages, services, and utilities like cable trays, HVAC ducts, and firefighting pipes (Fig. 1). These are referred to as Non-Structural Elements (NSE).  The majority of residential buildings, as well as nearly all commercial buildings, have their building services suspended from the ceiling via a supporting structure. In the event of an earthquake, failure of these systems could result in fatalities, costly repairs, obstruction of escape routes endangering people's safety, and in certain situations, hinder the effective functioning of structures such as hospitals, data centers, airports, etc. The provisions in the National Building Code 2016 [1] clearly highlight the need for structural safety of the supports for mechanical, electrical and plumbing (MEP) systems.  According to National Building Code 2016, the NSEs should be securely fastened to the primary structure to prevent them from toppling over and hurting building occupants or blocking escape routes during an earthquake. Following an earthquake, the services and equipment meant to ensure the safety of the building's occupants—such as emergency lighting and fire suppression—should keep working. After a strong earthquake, NSEs that are vital to the operation of important structures, such as hospitals, airports, emergency response centers, data centers, and structures essential to the country's defense, should keep working. In the case of tall structures, IS 16700 [2] also makes similar suggestions.  The proposed modification of IS 1893 [3] addresses these requirements and makes it evident that non-structural elements—referred to in the standard as architectural elements and utilities—have adequate performance. The majority of projects do not yet employ sufficient safety measures for the NSEs, and conventional support systems are used instead, which are only intended to withstand gravity loads and do not take seismic induced forces into account.

A project was undertaken to study the behavior of NSEs supported using conventional and braced supports, when subjected to seismic excitation and, through the findings, instill a strong sense of awareness among the sector regarding the importance of implementing a well-designed support system.

Fig. 1. Typical NSEs in a building

## Research Significance

The primary objective of the research project was to evaluate the seismic performance of non-structural support systems subjected to seismic excitation earthquakes. The study was expanded to include an analysis and comparison of the effectiveness of conventional systems used to support building utilities with a system sufficiently engineered to resist moderate to severe earthquake forces.

# Experimental Methodology

A three-story steel building with utility services installed on each floor was constructed as part of the test program, and the system was then put through an earthquake simulation on a shake table (Fig. 2). Non-structural components of the structure, such as cable trays, firefighting pipes, and multiple pipes, were supported by both conventional and braced support systems and suspended from the soffit of the slab at each floor level.

Fig. 2. Experimental set-up

## Test Specimen

### The G+2 story steel frame (2 m x 2 m x 9 m) was erected. Two ISMC 75 toe-to-toe connections for the battened columns and two ISMC 75 back-to-back connections for the beams were considered during the design process. The steel grade complied with E250 of IS 2062 [4]. The thickness of the slab at each floor was 100 mm. All connections were welded, using stick welding, to facilitate erection and in accordance with the resources at hand. Mild steel base plate measuring 3.5 m x 3.5 m was provided below test specimen and anchored to the shake table platform with the help of the high-tension bolts. The frame was designed to be sufficiently flexible to be able to transfer enough vibrations to the utility systems. The fundamental period for the frame was targeted at one second.

Three types of building utility, namely cable tray, sprinkler pipes and multiple pipes (Fig. 3) were installed. On the first floor, 1 no. 200 dia. and 1 no. 100 dia. metal pipes were installed. On the second floor, 1 no. 150 dia. was installed. On the third floor, 2 nos. 450 wide cable trays were installed. The pipes were filled with equivalent weight of water and cable trays filled with equivalent weight of cables, using sand.

Each building utility was supported using two parallel support system types. The first system was the conventional system generally adopted in practice, comprising of threaded tie rod and channel. While the second system consisted of bracings (rods, hanging wires and modular channels) and seismic connectors with modular supports designed to withstand seismic acceleration.

Fig. 3. Different utility systems at each floor

Design of Support for NSE. The support systems for each utility system were designed for adequacy against gravity load for the conventional system and earthquake load for the braced systems. The lateral force for the design of NSEs were calculated as per IS 16700 [2] assuming building to be in seismic zone V (i.e., Z = 0.36). A typical arrangement for cable tray support system is shown in Fig. 4. Summary of the design details for cable tray is shown in Fig. 5 and Fig. 6. Similar exercise was carried out for each utility system.

Fig. 4. Typical support system for cable tray

Fig. 5. Design of cable tray support against gravity load

Fig. 6. Design of cable tray support against seismic load

## Loading Protocol

## The entire assembly was subjected to base excitation on a 15-ton payload capacity shake table and the response of both support systems were observed. Only horizontal excitation was used in the present study to maintain line of sight alignment of non-contact optical/infra-red measurement system for monitoring horizontal response.

## The test was carried out in four steps consisting of excitation in a sinusoidal pattern of starting from an amplitude of 25 mm in the first step and going up to 100 mm in the final one, with a regular increment of 25 mm. Each step lasted for a duration of nearly 30 seconds and frequency of sinusoidal wave was kept of constant value of 0.6 Hz considering that the natural frequency of the frame was about 0.9 Hz with a tuning ratio of 0.67 and a dynamic amplification of approximately 2.0. A graphical representation of the loading protocol adopted for the test is shown in Fig. 7. The peak base acceleration corresponds to 0.036 g, 0.072 g, 0.109 g, and 0.145 g for these four test cases.

Fig. 7. Graphical representation of loading protocol.

## Instrumentation

The instrumentation included non-contact infra-red (IR) sensors to measure the displacement of utilities attached to the soffit of each slab. Uniaxial accelerometers were installed to measure floor acceleration of all floors, and strain gauges were used to measure strain at critical locations during the excitation. Infra-red sensors of the 3.5 m range were placed on a wooden panel supported by scaffolding such that each wooden panel was located at the level of the utility at the respective floor and adjusted to record the displacement of the corresponding utility. The reflector surface was prepared with white colored surface of 450 mm x 450 mm dimension. The IR sensors and the data acquisition system used for those sensors are shown in Fig.  8(a) and Fig.  8(b), respectively. Six IR sensors and three accelerometers were provided, as shown in Fig. 9. Out of three accelerometers, two triaxial accelerometers were placed on the 2nd and 3rd-floor slab and a uniaxial accelerometer was deployed on the first-floor slab (Fig. 10). Strain gauges as shown in Fig. 11 were provided at critical locations: 100 mm from the gusset plate provided at the base of columns on the tension and compression flanges of the columns and 100 mm from beam-column connections on tension and compression flanges in the 1st and 2nd-floor beams along the direction of excitation.

| (a) | (b) |
| --- | --- |

Fig. 8. (a) IR sensor set to incident beam on the reflector (b) data acquisition system.

Fig. 9. IR sensor and Accelerometer location details.

| (a) | (b) |
| --- | --- |

Fig. 10 (a) Triaxial accelerometer placed on slab (b) Image of the data acquisition system.

| (a) | (b) |
| --- | --- |

Fig. 11. An image of the strain gauge provided in the column near the gusset plate (b) An image of the data acquisition system to record strain gauge data.

# Test Results and Discussions

The data recorded by the sensors along with corresponding Fourier transforms in loading step number 1, 2, 3, 4, respectively are shown in Fig. 12 to Fig. 15. In each FFT plot, a peak at near 0.6 Hz was observed which corresponds to the excitation frequency. Another peak was observed at near 0.9 Hz which was near the natural frequency (1.1 s natural period) of the steel frame determined by its eigen value analysis considering self-weight and weight of utilities has been lumped at the floor levels, and stiffness of steel frame. Natural frequencies corresponding to conventional and designed braced support systems of utilities were obtained from the FFT plots of IR data. The slippage of anchor rod at one of the support points in the conventional cable tray support system in 3rd step led to decrease in initial peaks. Damage of the conventional cable tray support system occurring in 4th loading step resulted in partial decoupling of the NSE from the structural frame and manifested as the absence of a peak corresponding to natural period of the steel frame as shown in Fig.  15(f).

The data in CH2 corresponds to the displacement of conventional multiple pipe support assembly at the first floor while CH1 data shows the displacement of braced support assembly. The data in CH4 corresponds to the displacement of conventional single pipe support assembly at the second floor while CH3 data shows the displacement of braced pipe support assembly. The data in CH5 corresponds to the displacement of conventional cable tray support assembly at the third floor while CH6 data shows the displacement of braced support assembly.

Fig.  12. Data recorded by IR sensors in 1st loading step along with their Fourier  transform

Fig.  13. Data recorded by IR sensors in 2nd loading step along with their Fourier  transform

Fig.  14. Data recorded by IR sensors in 3rd loading step along with their Fourier  transform

Fig.  15. Data recorded by IR sensors in 4th loading step along with their Fourier  transform

The vibration amplitudes of conventional support system at the third-floor increased by an order of magnitude after the loss of support at one end while the braced system response remained under reasonable limits.

Floor acceleration was recorded with the help of the accelerometers installed at the top of each steel frames slab as shown in Fig.  16. It was able to record total acceleration values in m/s2 experienced by the steel frame at the floor level. Data recorded by accelerometers located at the top and 2nd floor along with FFT is shown in Fig. 16 and 17 respectively. From loading step number 1 to 4, amplitude of vibration increased in both the accelerometers. In acceleration data a sudden increase in amplitude was observed which may be attributed to the jerk experienced by entire test-specimens due to sudden start and stoppage of the shake table.

Fig .16. total acceleration record of top floor accelerometer and corresponding FFT plot (a) in loading step 1 (b) loading step 2 (c) loading step 3 (d) loading step 4

Fig. 17. Total acceleration record of middle floor accelerometer and corresponding FFT plot in (a) loading step 1 (b) loading step 2 (c) loading step 3 (d) loading step 4

Strain gauges recorded the strain values in all loading steps.  It was found that all the values were less than the yield strain corresponding to mild steel which is 0.0125. Similar results were found in loading steps 2 and 3 increase in maximum strain. The strain value in SG L12 located on the first-floor beam was found to exceed the yield value in loading step 4. The accelerometers were deployed on the center point of the floor. The damage of the NSE supporting system can affect the mass distribution and hence can have some effect on the eccentricity between the center of mass and the center of stiffness. There was a consistent reduction in the amplification of base acceleration at different floor levels for the third and fourth loading cycle. Particularly, the reduction in the response of the second floor level is intriguing. The flattening of the Fourier amplitude spectrum in the second and third floor acceleration response implies increased damping of the system due to the contents of the non-structural elements at the enhanced level of shaking.

Fig. 18. Maximum story total acceleration by dynamic analysis and those recorded by accelerometers in each loading step

In the test set-up, the sprinkler system pipes on the second floor were filled with sand and aggregates to simulate the weight of water in the actual sprinkler systems. Due to higher density of sand and aggregates, the sprinkler pipes were only partially filled and at the enhanced level of base motions, the shifting of sand and aggregates in these pipes in response of vibrations led to enhanced damping in the system which was reflected in the reduced system response at the higher levels of base motion and also in the flattening of the response peak in the vicinity of structural frequency of 0.9 Hz in the Fourier amplitude spectra.

## Observations

In loading step number one, there was nominal vibration, and no damage was observed in the utility supports. The difference in the amplitude of vibration between the conventional and the braced support systems was visually discernible with the conventional system having visibly large amplitude oscillations. The movement of the cable tray supports at the third storey was largest, followed by sprinkler system at the second storey and the least sway was observed for the multi-pipe supports at the first floor. Similar behaviour was observed for step two of loading.

In loading step number three, loosening of anchor and consequent tilting of the cable tray supported by the conventional system located at the top floor was observed (Fig. 12). No other damage was observed apart from the conventional support of the cable tray on the third storey. Significant sway was observed in the conventional sprinkler support system, as compared to the braced support at the second storey.

Fig. 19. Tilted cable tray supported by the conventional system

In the final loading sequence, the conventional cable tray support suffered a collapse due to the failure of both the support points on the same side (Fig. 13). This was an outcome out of eccentric loading being generated subsequent to yielding at one support point in the previous loading cycle. It was observed that the braced cable tray support system was much stiffer and did not suffer any damage during the shaking.

From these results it can be inferred that the conventional system was far more flexible than the braced system. Excessive displacement of the conventional suspension support system can have implications for the required clearance during installations to accommodate possible large displacements during seismic events.

Fig.  20. (a) Damaged conventional cable tray (b) failure of cable tray system due to slippage of threaded rod (c) undamaged braced cable tray system

# Conclusion and Recommendations

From the said test program, it is evident that failure can occur in any component of the entire support system – the bracing, the vertical support, the connectors or the anchor connecting the whole arrangement to the parent structure and the behaviour cannot be predicted beforehand. Hence every element of the support system should be given dure consideration and should be seismically designed. Even drift limits on the suspension/support systems for NSEs need to be prescribed in design specification to avoid any secondary failure due to pounding during a seismic event.

Various building codes and standards of the country recommend designing building utility supports such that they remain functional post an earthquake, especially for important buildings. Despite this requirement, most NSE supports are not adequately designed in practice. In most cases, conventional supports systems without seismic bracing are employed to resist gravity loads only. It is clear from the finding of this research project that conventional systems may not be suited when the building utilities are expected to resist seismic excitation. Similar studies have been carried out in different parts of the world that document the inadequacy of conventional support systems for seismic conditions. It is important to step away from conventional systems and embrace systems, such as modular supports with bracing, which are more suited for resisting seismic excitation. There is a need to develop comprehensive standards for design of modular system with seismic bracing.

# Acknowledgements

We are extremely thankful to Hilti India Pvt. Ltd. for giving us the opportunity to work on the project that involves a very pertinent topic related to safety. We are grateful to Earthquake Engineering Department, Indian Institute of Technology (IIT) Roorkee for their guidance and support in undertaking this extensive work. Findings, opinions, and conclusions are those of the authors.

# References

Xiang Wang, Hamed Ebrahimian, Rodrigo Astroza, Joel P. Conte, Jose I. Restrepo, and Tara C. Hutchinson (May 2013) “Shake Table Testing of a Full-Scale Five-Story Building: Pre-test Simulation of the Test Building and Development of an NCS Design Criteria”

Goutam Mondal and Sudhir K Jain, The Indian Concrete Journal, (2005) “Design of non-structural elements for buildings: A review of codal provisions”

FEMA E-74 (2011) “Reducing the Risks of Nonstructural Earthquake Damage – A Practical Guide”

Matthew S. Hoehler, M.EERI, Shojiro Motoyui, Kazuhiko Kasai, Yasuaki Sato, Tsuyoshi Hikino, and Kosuke Hirase, Earthquake Spectra, Volume 28 (2012), “Ceiling Anchorage Loads during Shake Table Tests of a Full-Scale Five-Story Building”

NIST GCR 17-917-44, “Seismic Analysis, Design, and Installation of Nonstructural Components and Systems – Background and Recommendations for Future Work”

National Building Code of India, 2016

IS 1893:2016 “Criteria for Earthquake Resistant Design of Structures”

IS 16700-2017 Criteria for Structural Safety of Tall Concrete Buildings”

National Disaster Management Guidelines – Hospital Safety